## Slide 1: Electrical Hazards
Notes: Upper Right Photograph shows a concrete boom/pumper truck burned after contact with overhead power lines

## Slide 2: Learning Objectives
Understand hazards associated with;
  Installation of temporary power
  Working around electrical panels
  Arc Flash
  Work around overhead power lines
  Lightning
Identify OSHA requirements related to electrical hazards in construction.
Discuss how to manage electrical issues on job sites

## Slide 3: Temporary Wiring and Lighting Systems

## Slide 4: Electrical Harm
PATH: Harm is related to the path by which current passes through the body.
Notes: Describe how even small levels of amperage can cause serious injuries by affecting the electrical system of the body and affecting the heart rhythm.

## Slide 5: Ground Fault Circuit Interrupters (GFCI)
Monitors current flow between the hot and neutral wires
Trip between 4-6 mA in 1/40th of a second
GFCI with open neutral protection must be used on a construction site.
Notes: Describe how GFCIs work.
Advise that they must be tested regularly.

## Slide 6: Assured Equipment Grounding Program
Inspection is your primary protection
Best practice recommends documented testing every 3 months
Color coding most common:
Winter
Spring
Summer
Fall
Notes: Advise that testing should be done regardless of whether GFCIs are in use.

## Slide 7: Reverse Polarity Diagram
Hot
Neutral
Switch
Tool could be hot with the switch off
Hot wire and neutral wire are reversed
Even though a switch is off, the circuit could be hot

## Slide 8: Electrical Extension Cords
The primary insulation is cut
If the insulation was also cut on the conductors, exposing bare wires, they could come in contact with someone
Damage is often caused by repeated stretching or being run over
Notes: This cord is out of compliance and must be removed.
Describe types of damage cords can have and what to look for.
See Additional Resources for additional guidance on letter of interpretation for nicks and GFCI

## Slide 9: Extension Cord Plug Strain
Strain Relief Needed

## Slide 10: Extension Cords
Place cords where they will not be run over by traffic or equipment.
Protect cords from run over by trucks, scissors lifts, etc.

## Slide 11: Portable Generators
Portable generators need to be grounded per manufacturer’s requirements.
Plug grounds are bonded to the frame.
Outlets should be GFCI’d

## Slide 12: Electrical
Wiring like this must be protected in closed boxes
There is the potential of electric shock from loose wire nuts or exposed conductors
Notes: This wiring cannot be left exposed.
Stress that all electrical wire must be properly protected inside electrical boxes.

## Slide 13: Temporary Lights
Lights must have bulbs. NO OPEN SOCKETS!
Cages must be supported. DO NOT HANG ON PIGTAIL WIRES!
Light strings should not be made up with just two conductor wires. There is no strain relief.

## Slide 14: Temporary Lights
Always keep cages closed.
If romex is used as the power cord, it must be better supported and secured.

## Slide 15: Suspending Temporary Lights
Light cages must be suspended by other means than just hung on the wire nut connection.
If something caught a cage, it could pull the wire nut connection apart, exposing employees to live wires.

## Slide 16: Temporary Lights
This is a good installation.
The lights are in bonded connections and run with a hard service cord.
The cages still need to be supported.

## Slide 17: Electrical Panel Boxes
Live electrical panels must be completely covered with a hard cover (original intended equipment)
Employees could be exposed to live wires around the perimeter of this box
No Cardboard!
Notes: This is not considered protected.
Stress the need for all live circuitry to be covered or protected.
Electricians cannot leave panel boxes unattended with the covers off.

## Slide 18: Open Panel Boxes
This is a bad installation.
Boxes need to be completely covered so no electrical connections are exposed.

## Slide 19: Arc Flash Prevention

## Slide 20: An electric arc:
Typically lasts less than a second
Has extremely high radiant (heat) energy
Is explosive in nature (exerts great force)
Can ignite or melt conventional work clothing

## Slide 21
Notes: These pictures are from an Arc-flash accident.
Note the burned clothing.
Note that the chest was protected by a shirt and the bows of the glasses protected a strip on the head.

## Slide 22: Electrical Arc
Pressure Waves > 2000 lb/psf
Copper Vapor:
Solid to Vapor
Expands by
67,000 times
Molten Metal > 1800 ° F
Intense Light
Hot Air >500 ° F
35,000 °F
Shrapnel > 740 mph
Sound Waves >140db
Notes: Describe the physics of an electric arc.

## Slide 23: NFPA 70E Requirements
Arc flash boundaries must be known
Safe approach distances established and maintained
Marking equipment relative to hazards
Electrically safe (voltage rated) tools
PPE (ATPV)
Training
Notes: Refer to the Arc Thermal Protective Value (ATPV).

## Slide 24: DON’T Work with Energized Electrical Equipment
Shut it down and lock it out
Establish an electrically safe working condition
Live work can only be done when authorized by a qualified person and the owner of the facility (documentation required), and then ONLY when it may create a greater hazard to shut the power off, such as in a life-safety situation
ALL appropriate protective measures must be taken, and documentation must be maintained
Notes: Discuss that the best procedure is always to shut the system down, lock it out and eliminate the hazard.

## Slide 25: Overhead Powerlines

## Slide 26: Power Line Facts
Overhead lines are typically not insulated.
Over 90 percent of the contacts occur on overhead distribution lines
Operators are normally safe if they stay on the equipment
Ground personnel are over 8 times more likely to be killed

## Slide 27: Electrical Damage to the Body
If you touch a power line, electricity will attempt to travel through your body
When electricity travels through the body, it heats up and burns body tissue internally
Electricity leaves the body violently, causing burns or even blowing an exit hole
Notes: Discuss the devastating injuries these contact accidents create.

## Slide 28
Notes: This dump truck contacted an overhead power line.
The rear outside drive tires were blown off of the hubs by the electrical voltage as it passed through the tires and heated them up causing them to expand.
One tire flew nearly sixty feet – causing an additional struck-by hazard!

## Slide 29: Power Lines
You must assume that all power lines are energized unless the utility company confirms that the power line has been de-energized and visibly grounded at the worksite.

## Slide 30: Crane Clearances
Notes: No proximity alarms or Insulating links are currently approved. A temporary enforcement policy was established on March 31, 2014 establishing enforcement criteria for bot devices.
Proximity Alarms
Because no current proximity alarms meet the NRTL requirements, employers may not rely solely on proximity alarms to comply with the requirements of the cranes standard. However, an employer may use a crane/derrick in construction with a proximity alarm in conjunction with another appropriate "measure" from §§ 1926.1407(b)(3) or 1926.1408(b)(4), such as a "dedicated spotter" or "range control warning device." If these conditions are met, the employer will not be considered to be in violation of either §§ 1926.1407(b)(3) or 1926.1408(b)(4), including situations where voltages are over 350 kV as referenced in § 1926.1409.
March 31, 2014
MEMORANDUM FOR: REGIONAL ADMINISTRATORS
FROM: JAMES G. MADDUX
SUBJECT: Temporary Enforcement Policy for Proximity Alarm and Insulating Link Use with Cranes and Derricks in Construction
Effective April 30, 2014, until further notice, the Occupational Safety and Health Administration (OSHA) intends to follow the temporary enforcement policy described below for use of proximity alarms and insulating links with cranes or derricks while engaged in construction activities near power lines. OSHA initially adopted a temporary enforcement policy for the use of these devices in a June 25, 2012 memorandum, and it was effective July 26, 2012 through November 8, 2013. This memorandum supersedes OSHA's June 25, 2012 memorandum.
The Cranes and Derricks in Construction standard, 29 CFR 1926 Subpart CC ("cranes standard"), includes several options for cranes and derricks performing construction activities near power lines. Some of the options involve proximity alarms or insulating links/devices. Section 1926.1401 of the cranes standard defines "proximity alarm" and "insulating link/device" as devices that warn of proximity to power lines or that insulate against electricity and that have been "...listed, labeled or accepted by a Nationally Recognized Testing Laboratory in accordance with § 29 CFR 1910.7" ("NRTL requirements"). These pieces of safety equipment must meet the performance requirements and the NRTL requirements as defined in § 1926.1401-Definitions to be used on cranes and derricks in construction.
To date, no proximity alarm or insulating link/device meets the NRTL requirements. Additionally, at this time, no NRTL is recognized by the Agency to perform the required testing to list, label or accept either type device. Proximity alarms and insulating links/devices which do not meet the NRTL requirements continue to be available, as they have for decades. These versions have not been "...listed, labeled or accepted by a Nationally Recognized Testing Laboratory." OSHA does not anticipate proximity alarms or insulating links/devices which meet the NRTL requirements to be available in the near future.
Because there are no compliant proximity alarms or insulating links/devices, OSHA intends to follow the temporary policy noted below until further notice and will engage in rulemaking to address the unavailability of proximity alarms and insulating links/devices which meet these NRTL requirements. The temporary policy is for:
proximity alarm use under § 1926.1407-Power line safety (up to 350 kV)-assembly and disassembly;
proximity alarm and insulating link use under § 1926.1408-Power line safety (up to 350 kV)-equipment operations;
proximity alarm and insulating link use under § 1926.1409-Power line safety (over 350 kV) through §§ 1926.1407 and 1926.1408; and
insulating link/device use under § 1926.1410-Power line safety (all voltages)-equipment operations closer than the Table A zone.
Insulating Links/Devices
Because no current insulating links/devices meet the NRTL requirements in the § 1926.1401 definition for "insulating link/device," employers may not rely solely on an insulating link/device to comply with requirements of the cranes standard. However, an employer may use a crane/derrick in construction with an insulating link in conjunction with another appropriate "measure" from § 1926.1408(b)(4), such as a "dedicated spotter" or "range control warning device." If these conditions are met, the employer will not be considered to be in violation of § 1926.1408(b)(4), including situations where voltages are over 350kV as referenced in § 1926.1409. Additionally, OSHA will not cite any employer for a violation of § 1926.1410(d)(4) (requirement that an insulating link/device be "installed at a point between the end of the load line (or below) and the load") if an employer is using an insulating link/device manufactured on any date, as specified in § 1926.1410(d)(4)(v)(A), and in conjunction with the additional protections in § 1926.1410(d)(4)(v)(B), such as insulated gloves rated for the voltage involved.

## Slide 31: Table A Minimum Clearance Distances
up to 50kv 10 feet
over 50 to 200kv 15 feet
over 200 to 350kv 20 feet
over 350 to 500kv 25 feet
over 500 to 750kv 35 feet
over 750 to 1,000kv 45 feet

## Slide 32: Option 2 & 3 – Signs and/or barriers

## Slide 33: Maintain Safe Working Clearance
All equipment – ladders, scaffolds, trucks, forklifts, etc. – MUST maintain a minimum 10 foot clearance from 50 kV or less
Add .4 inches for every kV over 50 kV
Notes: ANSI guidelines suggest the following distances, which are greater than OSHA requirements:
  100 kV - 15 feet
  350 kV - 20 feet
  500 kV - 25 feet
Why do distances increase with voltage?
Load sag and flex are primary issues on transmission lines

## Slide 34
MINIMUM 10' Distance
Notes: Discuss that the 10 foot minimum clearance applies to all types of equipment.

## Slide 35: Ensure Adequate Clearance
Install flag warnings at proper distances
If it is difficult for an operator to see the power lines, designate a spotter
If you cannot maintain adequate clearances, you must have the power company insulate, move or de-energize the line
Notes: Discuss the various methods.
Also discuss the fact that it may take a power company several weeks to de-energize or move a line.
Therefore proper pre-planning is a MUST.

## Slide 36: Barrier Protection
Insulated Sleeves Must be Installed by the Utility Company
Allow Sufficient Time
Must Still Maintain Minimum Line Clearance Distance
Insulated Sleeve
Insulated Blanket
Note: insulated sleeves can be damaged by a wire rope used for hoisting
Notes: Barrier Protection:
Insulated Sleeves Must be Installed by the Utility Company. This shall not be done by the contractor.
Allow Sufficient Time. This may require several weeks advance notice.
Must Maintain Minimum Line Clearance Distance

## Slide 37: If Contact Occurs
Stay on the machine if possible
Warn all others to stay away
Notify power company immediately
Attempt to move away but assure line is not “connected”
Notes: Power distribution systems many times have storm trip circuits on them.
These are relays that will trip out for a period of time (Usually 3-30 seconds) to allow a faulted object such as a tree branch to fall away.
These relays will than reset and the line will be re-energized.
This may occur 2-3 times before a breaker actually trips and the power remains out until it is manually reset.

## Slide 38: The Ground May Be Hot!
Electricity dissipates with the resistance of the ground.
As potential drops, fields develop around the electrified machine.

## Slide 39: Bail Out Procedures
If you must get out, jump with your feet together
Do not touch the machine
Hop or shuffle out of the area

## Slide 42: Lightning Safety
Have a lightning safe policy!
If you see Lightning, seek shelter immediately!
Cranes - lower boom and stop operations and move to shelter
Those people who are working at heights - climb down and take shelter in a protected building / safe area

## Slide 43: Incident Free
Planning
  Installation of temporary power
  For working around electrical panels
  Work around overhead power lines
Training
  Workers about circuit contact
  For Arc-flash prevention and protection
  For safe work around overhead power lines
Inspection
  Electrical tools and equipment
  Electrical panels for live circuits
  Temporary wiring & lighting

## Slide 44: Incident Free
Oversight
  Electrical installations
  Site issues around power lines
Lessons learned
  Accidents with circuit contacts
  Arc-flash incidents
  Power line contacts
Re-evaluate
  Temporary electric specifications
  Electrical work practice
Notes: Use these steps to provide continuous improvement